## Condensation
Pump Parameters					Calculation for 1 to 3 Pumps with simple valve Characteristic
totalHead	14	bar	1.40E+06	Pa
workingPressure	8	bar	8.00E+05	Pa			Resistance	Valves and	Total Resistance (Valves + Plant) with…			Resulting Flow
workingFlow	600	kg/s				Valve Open	per Valve	Plant Res.	1 Pump	2 Pumps	3 Pumps	1 Pump	2 Pumps	3 Pumps
				0.1	900000	450450	452450	451450	451116.666666667	4.53088739087192	4.54092369033116	4.54427901134222
Pums in series:	2					10	9000	4950	6950	5950	5616.66666666667	294.964028776978	344.53781512605	364.985163204748
				20	4500	2700	4700	3700	3366.66666666667	436.170212765957	554.054054054054	608.910891089109
flowResistance	2000	Pa*s/kg				30	3000	1950	3950	2950	2616.66666666667	518.987341772152	694.915254237288	783.43949044586
2 Pumps:	1000	Pa*s/kg				40	2250	1575	3575	2575	2241.66666666667	573.426573426573	796.116504854369	914.498141263941
3 Pumps:	666.666666666667	Pa*s/kg				50	1800	1350	3350	2350	2016.66666666667	611.940298507463	872.340425531915	1016.52892561983
				60	1500	1200	3200	2200	1866.66666666667	640.625	931.818181818182	1098.21428571429
Valve Configuration					70	1285.71428571429	1092.85714285714	3092.85714285714	2092.85714285714	1759.52380952381	662.817551963049	979.522184300341	1165.08795669824
Parallel Valves	2					80	1125	1012.5	3012.5	2012.5	1679.16666666667	680.497925311203	1018.63354037267	1220.84367245658
				90	1000	950	2950	1950	1616.66666666667	694.915254237288	1051.28205128205	1268.0412371134
Simple Chacacterisitc:					100	900	900	2900	1900	1566.66666666667	706.896551724138	1078.94736842105	1308.51063829787
resistanceFullOpen	900	Pa*s/kg

Advanced Characteristic:
flowOpen	620	kg/s				Calculation for 1 to 3 Pumps with advanced valve Characteristic
effort	20	bar	2.00E+06	Pa
resistance	2500	Pa*s/kg					Resistance	Valves and	Total Resistance (Valves + Plant) with…			Resulting Flow
				Valve Open	per Valve	Plant Res.	1 Pump	2 Pumps	3 Pumps	1 Pump	2 Pumps	3 Pumps
Plant parameter					0.1	3223306.4516129	1612103.22580645	1614103.22580645	1613103.22580645	1612769.89247312	1.27005507902121	1.27084241554047	1.27110507801978
				10	29758.064516129	15329.0322580645	17329.0322580645	16329.0322580645	15995.6989247312	118.298585256888	125.543263532201	128.159451465448
resistance (total)	450	Pa*s/kg				20	13629.0322580645	7264.51612903226	9264.51612903226	8264.51612903226	7931.18279569893	221.274373259053	248.048399687744	258.473427331887
backPressure	7.5	bar	7.50E+05	Pa		30	8252.68817204301	4576.34408602151	6576.34408602151	5576.34408602151	5243.01075268817	311.723348593852	367.624373312765	390.996718621821
				40	5564.51612903226	3232.25806451613	5232.25806451613	4232.25806451613	3898.9247311828	391.800246609125	484.375	525.785990071704
				50	3951.61290322581	2425.8064516129	4425.8064516129	3425.8064516129	3092.47311827957	463.192419825073	598.399246704331	662.899860917942
				60	2876.34408602151	1888.17204301075	3888.17204301075	2888.17204301075	2554.83870967742	527.240044247788	709.791511541326	802.39898989899
				70	2108.29493087558	1504.14746543779	3504.14746543779	2504.14746543779	2170.81413210445	585.021041557075	818.641884431358	944.346164732522
				80	1532.25806451613	1216.12903225806	3216.12903225806	2216.12903225806	1882.79569892473	637.41223671013	925.036390101892	1088.80639634495
				90	1084.229390681	992.114695340502	2992.1146953405	1992.1146953405	1658.78136200717	685.134163871586	1029.05721482548	1235.84701815039
				100	725.806451612903	812.903225806452	2812.90322580645	1812.90322580645	1479.56989247312	728.784403669725	1130.78291814947	1385.53779069767
Simple Valve Characteristic
Reg. Valve Position (%)
Total Flow (kg/s)
Advanced Valve Characteristic
Reg. Valve Position (%)
Total Flow (kg/s)

## Feedwater Main
Pump Parameters
totalHead	95	bar	9.50E+06	Pa
workingPressure	65	bar	6.50E+06	Pa
workingFlow	388	kg/s
					Resistance	Valve and	Total R
					Valve Open	per Valve	Plant Res.	inc. Pump	Flow
					0.1	3746900	3747400	3755131.95876289	0.998633347957078
flowResistance	7731.9587628866	Pa*s/kg				10	34400	34900	42631.9587628866	87.9621792856625
					20	15650	16150	23881.9587628866	157.022296086853
					30	9400	9900	17631.9587628866	212.681985616558
					40	6275	6775	14506.9587628866	258.496633325635
Valve Parameters					50	4400	4900	12631.9587628866	296.866073614625
Advanced Characteristic:					60	3150	3650	11381.9587628866	329.468774059146
flowOpen	1200	kg/s				70	2257.14285714286	2757.14285714286	10489.1016200295	357.513935496553
effort	45	bar	4.50E+06	Pa		80	1587.5	2087.5	9819.4587628866	381.894775521988
resistance	3100	Pa*s/kg				90	1066.66666666667	1566.66666666667	9298.62542955327	403.285413356
					100	650	1150	8881.9587628866	422.204166908479
Plant parameter

resistance (total)	500	Pa*s/kg
backPressure	57.5	bar	5.75E+06	Pa

There are 2 pumps on each side with each having / one full load valve, on full load, flow will be 388.8 / kg/s, pressure in DA is 7.4 bar and 65 bar in drums. / This gives a pressure diff of 57.6 bar. / The calculation done for one valve with one pump / only. The second one in this chart just shows what / would happen if you only open one valve.
Advanced Valve Characteristic
Reg. Valve Position (%)
Total Flow (kg/s)

## Feedwater Startup
Pump Parameters
totalHead	95	bar	9.50E+06
workingPressure	65	bar	6.50E+06					Flow rate for each of the backPressue / variants that are given
workingFlow	388	kg/s				Valve Open	Valve R	with Plant-R	with Pump-R
					0.1	39996000	40001000	40008731.9587629	0.224950893451868	0.212453621593431	0.187459077876556	0.137469990442808	0.0749836311506225
flowResistance	7731.9587628866	Pa*s/kg				10	396000	401000	408731.958762887	22.0193205034429	20.7960249199183	18.3494337528691	13.4562514187707	7.33977350114763
					20	196000	201000	208731.958762887	43.1174988887243	40.7220822837951	35.9312490739369	26.3495826542204	14.3724996295748
Valve Parameters					30	129333.333333333	134333.333333333	142065.29209622	63.3511526087903	59.8316441305242	52.7926271739919	38.7145932609274	21.1170508695968
Advanced Characteristic:					40	96000	101000	108731.958762887	82.7723523276761	78.1738883094719	68.9769602730634	50.5831042002465	27.5907841092254
flowOpen	200	kg/s				50	76000	81000	88731.9587628866	101.429069362147	95.79412106425	84.5242244684559	61.9844312768677	33.8096897873824
effort	80	bar	8.00E+06			60	62666.6666666667	67666.6666666667	75398.6254295533	119.365571304863	112.734150676815	99.4713094207192	72.9456269085274	39.7885237682877
resistance	4000	Pa*s/kg				70	53142.8571428571	58142.8571428571	65874.8159057437	136.622772697802	129.032618659036	113.852310581502	83.4916944264348	45.5409242326008
					80	46000	51000	58731.9587628866	153.238546603476	144.725294014394	127.69878883623	93.6457784799017	51.0795155344918
Plant parameter					90	40444.4444444444	45444.4444444444	53176.403207331	169.24800206794	159.845335286388	141.040001723284	103.429334597075	56.4160006893135
					100	36000	41000	48731.9587628866	184.683731753755	174.423524434102	153.903109794796	112.862280516184	61.5612439179183
resistance (total)	5000	Pa*s/kg	of which 500 is shutoff valve
backPressure 1	5	bar	5.00E+05
backPressure 2	10	bar	1.00E+06
backPressure 3	20	bar	2.00E+06
backPressure 4	40	bar	4.00E+06
backPressure 5	65	bar	6.50E+06

		resistanceFullOpen
		for reduction valve:
		4500
Flows for different Drum Pressures
Startup Valve Position (%)
Flow